## Slide 1: Setup

## Slide 2
Lessons Learned From the 1998-2004
US Pirelli-Detroit Edison Cable Demonstration
Paul Michael Grant
EPRI Science Fellow (Retired)
IBM Research Staff Member/Manager Emeritus
(etc, etc...& so forth and so on)
W2AGZ Technologies
San Jose, CA 95123, USA (w2agz@w2agz.com)
Aging IBM Pensioner

## Slide 3: Grandson of Two Proud Lands
Bridget Ann Mullen-Whalen
Notes: 3

## Slide 4: Fathers of Electricity in America
Steinmetz Edison Tesla
Samuel Insull George Norris Chauncey Starr

## Slide 5: “Ancient History” “Those who cannot remember the past are condemned to repeat it” George Santayana
With the emergence of long distance telegraphic and electricity transmission throughout Europe and the US in the late 19th century, Pirelli in 1901 began exploitation of its rubber vulcanization IP to produce cables to service the emerging market.
Pirelli quickly came to dominate production and installation of electric power transmission cables in North America.
In the 1980s, Pirelli entered the market for fiber optic cables, again deploying similar production technology used for power lines.
Now it’s 1989. Pirelli spots a new opportunity (similar to that provided by fiber optics in communication) for commercialization of HTSC for electricity, especially in the US where it has dominated transmission cable deployment by American electric utilities for the previous seven decades.
Pirelli thus undertakes a collaboration with American Superconductor to develop Bi-2223 “OPIT” HTSC tapes as the conductor basis for a new generation of high-delivery cables.
It is important to note that this collaboration was initially funded by Pirelli, with later partial support from DOE and EPRI (i.e., NOT totally government sponsored!)
...more...

## Slide 6: ...Continued...
Pirelli’s vision: A market possibly exists for a “retrofit/replacement” HTSC transmission/distribution cable with the following idealized parameters:
  20-120 kV with the same form factor as conventional
  3 kA capacity (3x that of 1 kA conventional)
  2x cost of conventional
By mid-1993, a 50-m “warm temperature dielectric” prototype “mock up” cable and terminations, satisfying the above I/V characteristics was built using AMSC “Gen I” wire, partially funded by EPRI, and successfully tested at Pirelli’s South Carolina facility.
Now, a few pictures...

## Slide 7: “South Carolina” Photo Album

## Slide 9: “Middle Ages”
It’s now 1998. EPRI joins with Pirelli, AMSC, DOE, and Lotepro to propose an in-field demonstration of the WTD cable concept with investor-owned utility, Detroit-Edison (DECO, now DTE).
Why DTE?
  During the decades following the 1960s, the economy and infrastructure in downtown Detroit declined rapidly.
  However, with the advent of casino gambling in 1994 in neighboring Windsor, Ontario, it was anticipated that a new era of growth would occur in Detroit to service the tourist trade to follow that would pressure the aging urban electricity distribution network.
  DTE viewed the Pirelli WTD concept as a solution that could double or triple power delivery to mid-town Detroit within the existing underground duct facilities.
  DTE, established in 1908 and a founding member of EPRI, had a long established reputation as an early adopter of novel electric technologies.
DTE’s Frisbie substation, one of the earliest distribution substations in the US (1930), on the eastern metropolitan border of Detroit, was chosen as the demonstration site by reason of its ease of access and existing support facilities.
Installation of three cables, each approximately 120 meters long, and attendant cryogenic, splice joint and termination ancillary requirement, was completed in late 2001.
The intention was to operate each for 18 months, all the while monitoring performance, with subsequent removal and return to Pirelli to study any deterioration issues.

## Slide 10: “Milan-Frisbie” Photo Album

## Slide 12: “The Dark Age”
In late 1998, AMSC detected “blister/balloon” issues in its “Gen I” due to LN2 diffusion though the silver binder. These were fixed prior to cable manufacture.
However, after installation of the three WTD cables in Frisbie, it was found on initial “pump down,” leaks of various severity were discovered in all three phases. Two of the cables were returned to Pirelli for further analyses.
The remaining “third phase” cable exhibited “intermittent pressure instabilities” reaching roughly 5•10-2 torr.
Since the cable terminations shared their vacuum with the cable itself, this pressure represents roughly 10% of the Paschen discharge limit for gaseous N2 at the substation distribution voltage of 24 kV, it was deemed unsafe to energize and connect to the DTE local grid.
Subsequent metallurgical analysis of the stainless steel inner and outer corrugated vacuum barriers revealed microcracks, most likely caused by hydrogen embrittlement and amorhorphization induced by Pirelli’s use of its standard production methods employed in its conventional hermetically sealed cable products.

## Slide 13
Leaks emerged after pulling cable around the conduit bends

## Slide 14: “August, 2003 - A Brief Dawning”

## Slide 15: Why Did Pirelli “Park” HTSC Cable Development?
It was NOT due to the problems encountered at Detroit Edison!
Pirelli Timeline ($100 M, 1993 – 2002)
  1993 SPI for EPRI/Pirelli Proto
  1998-1Q SPI for Detroit Edison
  1998-4Q “Blister/Balloons” found in Proto
  2001
    May Pirelli submits LIPA SPI proposal to DOE
    July Pirelli offers Energy Cables for sale
    Sept SPI to Pirelli for LIPA
    Dec Leaks found at Frisbie
  2002 Pirelli withdraws from LIPA (business case needed, not more demos)
  2005 Pirelli sells Energy Cables to G-S (Prysmian)
Nota Bene! This slide was originally shown in my presentation, ”Quo Vadis High-Tc,” given at the DOE WDW, 31 January 2006!

## Slide 16: Is There a Mass(ive) Market for HTSC Cables?
Sale of Pirelli Cable Systems (now Prysmian) to Goldman-Sachs, July 2005
  12,000 Employees, 52 Plants (Energy + Telecom)
  Sale Price $1.7 B
2004 Revenue & Profit
  Revenue $4.2 B
  EBIT $144 M
  Profitability 3% !
Nota Bene! The “bullets” shown are also taken “word for word,” from my 2006 DOE WDW talk.

## Slide 17: Lessons Learned (at least in the US)
Deregulation (e.g., DTE) dis-encentified the IOUs from investing in new technologies without the opportunity to recover that investment with from subsequent energy savings.
Therefore, it is unlikely market opportunities will emerge for novel transmission technologies, such as HTSC, irrespective of cost reduction and energy savings.
Capital markets in the US are targeting the “microgrid” instead.
But maybe, just maybe the Dual Use of fossil fuel transport ROWs will offer a resurrection...stay tuned!

## Slide 18: “You can’t always get what you want…”
Notes: 18
18

## Slide 19: “…you get what you need!”
Notes: 19
19